## 3.0_Valve List
VALVE LIST
Project : AL NOUF 1 PROJECT
RFQ NO. : D00P-00CZH00-J30-0001
DESCRIPTION : MOV (GATE & GLOBE)
NO | P&ID NO. | VALVE TYPE | Q'ty | SYSTEM | UNIT NO. | SYSTEM CODE | SYSTEM SEQUENCE NO. | ITEM CODE | FIRST SEQUENCE NO. | TAG NUMBER | DESCRIPTION | SDT NO. (Design Table No.) | DESIGN CONDITION |  | FLUID | PIPE |  |  |  |  | BODY SIZE | VALVE RATING [#] | CONNECTION TYPE | TYPE |  |  |  |  | MATERIAL |  | FAIL POSITION | ACTUATOR TRAVEL TIME [SEC] | LEAKAGE CLASS | SET PRESSURE [barg] | MAKER | MODEL | EXPLOSION PROOF | REMARK
[13 empty] | PRESSURE [barg] | TEMP [degC] |  | PMC CLASS | RATING | Material [ASTM] | NB [mm] | Sch. |  |  |  | ACTUATOR | OPERATION MODE | BODY | BONNET | TRIM | BODY | TRIM
1 | D00P-10LBG10-M05-0001 |  | 2 | P&ID FOR AUXILIARY STEAM SYSTEM GROUP 10 | [6 empty] | AUX BOILER DISCHARGE GATE VALVE | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | 판정축 ③ · 귀속 AUX BOILER→(다분기)
2 | D00P-10LBG10-M05-0001 |  | 2 | P&ID FOR AUXILIARY STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE B | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
3 | D00P-10LBG10-M05-0001 |  | 2 | P&ID FOR AUXILIARY STEAM SYSTEM GROUP 10 | [6 empty] | #20 AUX. STEAM HEADER DISCHARGE GATE VALVE | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | 판정축 ③ · 귀속 #20 AUX. STEAM HEADER→(다분기)
4 | D00P-10LBG10-M05-0001 |  | 2 | P&ID FOR AUXILIARY STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE A | [12 empty] | MOTOR |  | GLOBE | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
5 | D00P-10MAN10-M05-0001 |  | 2 | P&ID FOR BYPASS STEAM SYSTEM GROUP 10 (1 OF 2) | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE B | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
6 | D00P-10MAN10-M05-0001 |  | 2 | P&ID FOR BYPASS STEAM SYSTEM GROUP 10 (1 OF 2) | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE C | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
7 | D00P-10MAN10-M05-0001 |  | 2 | P&ID FOR BYPASS STEAM SYSTEM GROUP 10 (1 OF 2) | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE A | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
8 | D00P-10MAN10-M05-0002 |  | 2 | P&ID FOR BYPASS STEAM SYSTEM GROUP 10 (2 OF 2) | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE C | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
9 | D00P-10MAN10-M05-0002 |  | 2 | P&ID FOR BYPASS STEAM SYSTEM GROUP 10 (2 OF 2) | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE A | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
10 | D00P-10MAN10-M05-0002 |  | 2 | P&ID FOR BYPASS STEAM SYSTEM GROUP 10 (2 OF 2) | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE B | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
11 | D00P-10LCM10-M05-0001 |  | 2 | P&ID FOR CLEAN DRAIN SYSTEM FOR GROUP 10 | [6 empty] | TO BLOCK #10 CONDENSER GLOBE VALVE B | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
12 | D00P-10LCM10-M05-0001 |  | 2 | P&ID FOR CLEAN DRAIN SYSTEM FOR GROUP 10 | [6 empty] | TO BLOCK #10 CONDENSER GLOBE VALVE A | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →BLOCK #10 CONDENSER
13 | D00P-10LCA10-M05-0001 |  | 2 | P&ID FOR CONDENSATE SYSTEM GROUP 10 (1 OF 2) | [6 empty] | CEP GATE VALVE | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | 판정축 ① · 귀속 CEP
14 | D00P-10LCA10-M05-0001 |  | 2 | P&ID FOR CONDENSATE SYSTEM GROUP 10 (1 OF 2) | [6 empty] | TO SAFE LOCATION GATE VALVE A | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
15 | D00P-10LCA10-M05-0001 |  | 2 | P&ID FOR CONDENSATE SYSTEM GROUP 10 (1 OF 2) | [6 empty] | TO SAFE LOCATION GATE VALVE B | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
16 | D00P-10MAJ10-M05-0001 |  | 2 | P&ID FOR CONDENSER AIR REMOVAL SYSTEM GROUP 10 | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
17 | D00P-10MAJ10-M05-0001 |  | 2 | P&ID FOR CONDENSER AIR REMOVAL SYSTEM GROUP 10 | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
18 | D00P-10MAJ10-M05-0001 |  | 2 | P&ID FOR CONDENSER AIR REMOVAL SYSTEM GROUP 10 | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
19 | D00P-10MAJ10-M05-0001 |  | 2 | P&ID FOR CONDENSER AIR REMOVAL SYSTEM GROUP 10 | [6 empty] | FROM CEP DISCHARGE HEADER GATE VALVE | [12 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
20 | D00P-10LBC40-M05-0001 |  | 2 | P&ID FOR CRH STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#11 CRH GATE VALVE A | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#11 CRH
21 | D00P-10LBC40-M05-0001 |  | 2 | P&ID FOR CRH STEAM SYSTEM GROUP 10 | [6 empty] | TO FLASH BOX HRSG#11 BD TANK GLOBE VALVE B | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →FLASH BOX HRSG#11 BD TANK
22 | D00P-10LBC40-M05-0001 |  | 2 | P&ID FOR CRH STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#11 CRH GATE VALVE B | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#11 CRH
23 | D00P-10LBC40-M05-0001 |  | 2 | P&ID FOR CRH STEAM SYSTEM GROUP 10 | [6 empty] | TO FLASH BOX HRSG#11 BD TANK GLOBE VALVE A | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →FLASH BOX HRSG#11 BD TANK
24 | D00P-10LBC40-M05-0001 |  | 2 | P&ID FOR CRH STEAM SYSTEM GROUP 10 | [6 empty] | HRSG#12 BD TANK GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ① · 귀속 HRSG#12 BD TANK
25 | D00P-10LBC40-M05-0001 |  | 2 | P&ID FOR CRH STEAM SYSTEM GROUP 10 | [6 empty] | FROM AUX STEAM GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
26 | D00P-10LBC40-M05-0001 |  | 2 | P&ID FOR CRH STEAM SYSTEM GROUP 10 | [6 empty] | TO CONDENSER FLASH TANK GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CONDENSER FLASH TANK
27 | D00P-10LBC40-M05-0001 |  | 2 | P&ID FOR CRH STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
28 | D00P-00GHC10-M05-0001 |  | 1 | P&ID FOR DEMINERALIZED WATER DISTRIBUTION SYSTEM (1 OF 2) | [19 empty] | MOTOR |  | MOV(GATE) | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
29 | D00P-00GHC10-M05-0001 |  | 1 | P&ID FOR DEMINERALIZED WATER DISTRIBUTION SYSTEM (1 OF 2) | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
30 | D00P-00GHC10-M05-0001 |  | 1 | P&ID FOR DESAL. WATER SUPPLY SYSTEM | [19 empty] | MOTOR |  | MOV(GATE) | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
31 | D00P-00GHC10-M05-0001 |  | 1 | P&ID FOR DESAL. WATER SUPPLY SYSTEM | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
32 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [6 empty] | FROM FUEL OIL UNLOADING TO FUEL OIL STORAGE TANK A GATE VALVE B | [12 empty] | MOTOR |  | GATE | [11 empty] | 판정축 ② · 귀속 FUEL OIL UNLOADING→FUEL OIL STORAGE TANK A
33 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [6 empty] | TO GT#12 GATE VALVE B | [12 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
34 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [6 empty] | FROM FUEL OIL UNLOADING GATE VALVE | [12 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
35 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [6 empty] | FROM FUEL OIL UNLOADING TO FUEL OIL STORAGE TANK A GATE VALVE A | [12 empty] | MOTOR |  | GATE | [11 empty] | 판정축 ② · 귀속 FUEL OIL UNLOADING→FUEL OIL STORAGE TANK A
36 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
37 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
38 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
39 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [6 empty] | GT#11 RETURN LINE DISCHARGE GATE VALVE A | [12 empty] | MOTOR |  | GATE | [11 empty] | 판정축 ③ · 귀속 GT#11 RETURN LINE→(다분기)
40 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [6 empty] | TO GT#12 GATE VALVE A | [12 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
41 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [19 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
42 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [6 empty] | GT#11 RETURN LINE DISCHARGE GATE VALVE B | [12 empty] | MOTOR |  | GATE | [11 empty] | 판정축 ③ · 귀속 GT#11 RETURN LINE→(다분기)
43 | D00P-00EGD00-M05-0002 |  | 1 | P&ID FOR FUEL OIL SUPPLY SYSTEM (2/2) | [6 empty] | TO WASTE OIL TANK GATE VALVE | [12 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
44 | D00P-11EKG10-M05-0001 |  | 4 | P&ID FOR GT FUEL GAS SUPPLY SYSTEM | [6 empty] | GT FUEL GAS TEMPERATURE CONTROL VALVE BALL VALVE B | [12 empty] | MOTOR |  | BALL | [11 empty] | 판정축 ① · 귀속 GT FUEL GAS TEMPERATURE CONTROL VALVE
45 | D00P-11EKG10-M05-0001 |  | 4 | P&ID FOR GT FUEL GAS SUPPLY SYSTEM | [6 empty] | FUEL GAS HEATER A BALL VALVE B | [12 empty] | MOTOR |  | BALL | [11 empty] | 판정축 ① · 귀속 FUEL GAS HEATER A
46 | D00P-11EKG10-M05-0001 |  | 4 | P&ID FOR GT FUEL GAS SUPPLY SYSTEM | [6 empty] | GT FUEL GAS TEMPERATURE CONTROL VALVE BALL VALVE A | [12 empty] | MOTOR |  | BALL | [11 empty] | 판정축 ① · 귀속 GT FUEL GAS TEMPERATURE CONTROL VALVE
47 | D00P-11EKG10-M05-0001 |  | 4 | P&ID FOR GT FUEL GAS SUPPLY SYSTEM | [6 empty] | GT FUEL GAS TCV BALL VALVE | [12 empty] | MOTOR |  | BALL | [11 empty] | 판정축 ① · 귀속 GT FUEL GAS TCV
48 | D00P-10LBA10-M05-0001 |  | 2 | P&ID FOR HP STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#12 BD TANK GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#12 BD TANK
49 | D00P-10LBA10-M05-0001 |  | 2 | P&ID FOR HP STEAM SYSTEM GROUP 10 | [6 empty] | FROM HRSG#12 GATE VALVE | [12 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
50 | D00P-10LBA10-M05-0001 |  | 2 | P&ID FOR HP STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE C | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
51 | D00P-10LBA10-M05-0001 |  | 2 | P&ID FOR HP STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE B | [12 empty] | MOTOR |  | GLOBE | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
52 | D00P-10LBA10-M05-0001 |  | 2 | P&ID FOR HP STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN
53 | D00P-10LBA10-M05-0001 |  | 2 | P&ID FOR HP STEAM SYSTEM GROUP 10 | [6 empty] | FROM HRSG#11 GATE VALVE | [12 empty] | MOTOR |  | GATE | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
54 | D00P-10LBA10-M05-0001 |  | 2 | P&ID FOR HP STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#11 BD TANK BALL VALVE | [12 empty] | MOTOR |  | MOV(BALL) | [11 empty] | 판정축 ②b · 귀속 →HRSG#11 BD TANK
55 | D00P-10LBA10-M05-0001 |  | 2 | P&ID FOR HP STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE A | [12 empty] | MOTOR |  | GLOBE | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
56 | D00P-10LBC50-M05-0001 |  | 2 | P&ID FOR HRH STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#12 BD TANK GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#12 BD TANK
57 | D00P-10LBC50-M05-0001 |  | 2 | P&ID FOR HRH STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#11 BD TANK TO CLEAN DRAIN TANK GLOBE VALVE B | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#11 BD TANK TO CLEAN DRAIN TANK
58 | D00P-10LBC50-M05-0001 |  | 2 | P&ID FOR HRH STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE B | [12 empty] | MOTOR |  | GLOBE | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
59 | D00P-10LBC50-M05-0001 |  | 2 | P&ID FOR HRH STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#11 BD TANK TO CLEAN DRAIN TANK GLOBE VALVE A | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#11 BD TANK TO CLEAN DRAIN TANK
60 | D00P-10LBC50-M05-0001 |  | 2 | P&ID FOR HRH STEAM SYSTEM GROUP 10 | [6 empty] | FROM HRSG#11 REHEATER GATE VALVE | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
61 | D00P-10LBC50-M05-0001 |  | 2 | P&ID FOR HRH STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE A | [12 empty] | MOTOR |  | GLOBE | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
62 | D00P-11LAB00-M05-0001 |  | 4 | P&ID FOR HRSG FEEDWATER SYSTEM UNIT 11 | [6 empty] | TO HRSG#11 HP ECONOMIZER GATE VALVE A | [12 empty] | MOTOR |  | GATE | [11 empty] | 판정축 ②b · 귀속 →HRSG#11 HP ECONOMIZER
63 | D00P-11LAB00-M05-0001 |  | 4 | P&ID FOR HRSG FEEDWATER SYSTEM UNIT 11 | [6 empty] | TO HRSG#11 HP ECONOMIZER GATE VALVE B | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#11 HP ECONOMIZER
64 | D00P-11LAB00-M05-0001 |  | 4 | P&ID FOR HRSG FEEDWATER SYSTEM UNIT 11 | [6 empty] | HRSG #11 LP DRUM DISCHARGE GATE VALVE | [12 empty] | MOTOR |  | GATE | [11 empty] | 판정축 ③ · 귀속 HRSG #11 LP DRUM→(다분기)
65 | D00P-10LBA30-M05-0001 |  | 2 | P&ID FOR LP STEAM SYSTEM GROUP 10 | [6 empty] | TO CLEAN DRAIN TANK GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →CLEAN DRAIN TANK
66 | D00P-10LBA30-M05-0001 |  | 2 | P&ID FOR LP STEAM SYSTEM GROUP 10 | [6 empty] | FROM HRSG #11 GATE VALVE | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
67 | D00P-10LBA30-M05-0001 |  | 2 | P&ID FOR LP STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#11 BD TANK GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#11 BD TANK
68 | D00P-10LBA30-M05-0001 |  | 2 | P&ID FOR LP STEAM SYSTEM GROUP 10 | [19 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
69 | D00P-10LBA30-M05-0001 |  | 2 | P&ID FOR LP STEAM SYSTEM GROUP 10 | [6 empty] | FROM HRSG #12 GATE VALVE | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
70 | D00P-10LBA30-M05-0001 |  | 2 | P&ID FOR LP STEAM SYSTEM GROUP 10 | [6 empty] | TO HRSG#12 BD TANK GLOBE VALVE | [12 empty] | MOTOR |  | MOV(GLOBE) | [11 empty] | 판정축 ②b · 귀속 →HRSG#12 BD TANK
71 | D00P-00GKB10-M05-0001 |  | 1 | P&ID FOR POTABLE WATER SUPPLY SYSTEM | [6 empty] | FROM POTABLE WATER GATE VALVE | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | 판정축 ②a · 귀속 POTABLE WATER→
72 | D00P-00PAB10-M05-0001 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (1 OF 3) | [6 empty] | TO TRAVELING BAND SCREEN D BALL VALVE C | [12 empty] | MOTOR |  | BALL | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
73 | D00P-00PAB10-M05-0001 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (1 OF 3) | [6 empty] | TO TRAVELING BAND SCREEN D BALL VALVE A | [12 empty] | MOTOR |  | BALL | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
74 | D00P-00PAB10-M05-0001 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (1 OF 3) | [6 empty] | TO TRAVELING BAND SCREEN D BALL VALVE B | [12 empty] | MOTOR |  | BALL | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
75 | D00P-00GHB10-M05-0001 |  | 1 | P&ID FOR SERVICE WATER DISTRIBUTION SYSTEM (1 OF 2) | [19 empty] | MOTOR |  | MOV(GATE) | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
76 | D00P-00GHB10-M05-0001 |  | 1 | P&ID FOR SERVICE WATER DISTRIBUTION SYSTEM (1 OF 2) | [6 empty] | FROM DESALINATION PLANT GATE VALVE | [12 empty] | MOTOR |  | MOV(GATE) | [11 empty] | 판정축 ②a · 귀속 DESALINATION PLANT→
Note)
1. REFER TO ATTACHED REQUREMENT AND SPECIFICATION.
2. LEAKAGE CLASS: API 598
3. ENCLOSURE CLASS : IP67
4. ACTUATOR SHALL BE FITTED WITH A HANDWHEEL
5. ALL SIGNAL SHALL BE INTERFACED WITH DCS AS HARDWIRING
6. Each actuaotr shall be Factory Tested accroding to IEC standards with inspection report.
A final inspection record shall be supplied with each actuator.
This shall include the following information on general actuator data, nominal current, no load current, starting current, power factor at rated torque, output speed, torque setting, limit setting (turns/stroke), high voltage test, functional test (including all options) and visual inspection.
9. Noise Level Limit : < 80 dB(A)
10. Actuator torque shall be calculated based on 125% of Design Pressure.
11. Cable gland, cable gland adaptor and plug shall be provided for Purchaser's cable connection.

## 5.2.0 PKG Inter. Typical (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | Field IO
|  |  | PKG Interface / Field - DCS IO |  |  |  | SWGR/MCC Interface IO |  |  |  | to VMS / Vibration(Triad) Gas Detector(Triad)
PKG Q'ty | PACKAGE | TYPE | AI | AO | DI | DO | AI | AO | DI | DO | AI
| GT TCS #10 | TCS
| ST TCS #10 | TCS
| CEMS #10 | PLC
| VMS (MEB) #10 | VMS
| VMS (CT LEB) #10 | VMS
| VMS (CCR) | VMS
| Intake System PLC | PLC
| Tube Cleaning System for Condenser | PLC
| Tube Cleaning System for CCW | PLC
| Air Compressor | PLC
| HRSG PLC | PLC
| WTP | PLC
| WWT | PLC
| Gas Chlorination System | PLC
| CPP | PLC
| DCS | DCS
| GIS | PLC
| CWMU Chlorination System | PLC
| CT Chlorination System | PLC
↑ Control System 적용 PKG
| GT TCS #10 |  | 11 | 5 | 19 | 19
| ST TCS #10 |  | 17 | 0 | 10 | 13
| CEMS #10 |  | 9 |  | 3
| SWAS for HRSG #10 |  | 62 |  | 5 | 9
| Condenser Tube Leak Detection#10 |  | 4 |  | 1
| SWAS for Condensate #10 |  | 28 |  | 5 | 4
| SWAS for CW #10 |  | 2 |  | 3
| SWAS for CW Return Line #10 |  | 2
| QMS for HRSG Blowdown #10 |  | 1 |  | 3
| QMS for Process Holding Pond #10 |  | 3 |  | 1
| QMS for Discharge water to Chao Phraya river #10 |  | 11 |  | 3
| VMS (MEB) #10 |  | 34 |  | 34
| VMS (CT LEB) #10 |  | 120 |  | 120
| Bypass Valve HPU for HP #10 |  | 1 |  | 3
| Bypass Valve HPU for IP/LP #10 |  | 1 |  | 3
| HRSG Transmitter #10 |  | 1
| HRSG Level Switch #10 |  |  | 1
| HRSG CV (AI&AO) #10 |  | 1 | 1
| HRSG CV (DI) #10 |  |  |  | 2
| HRSG XV #10 |  |  |  | 2 | 1
| HRSG MOV #10 |  |  |  | 6 | 2
| HRSG MOV Inching #10 |  |  |  | 6 | 2
| HRSG MOV Inching (AI) #10 |  | 1
| HRSG Analog JB #10 |  | 158 | 25
| HRSG Digital JB #10 |  |  |  | 238 | 73
| ESDV #10 |  | 1 | 0 | 6 | 3
| Fuel Gas Supply System #10 |  | 1
| FG Condensate Tank for GT Area #10 |  | 1
| Condenser Vacuum Pump #10 |  | 2 |  | 14 | 7
| CEP SIGNAL JB (Vibration/ Temp) #10 |  | 7 | 0 | 1 | 1 | 1 |  | 6 | 2 | 7
| BFP |  | 14 | 0 | 2 | 1 | 1 |  | 6 | 2 | 11
| CWP SIGNAL JB (Vib./Temp) #10 |  | 5 | 0 | 1 | 1 | 1 |  | 6 | 2 | 9
| CCWP SIG JB #10 |  | 7 | 0 | 1 | 1 |  |  | 5 | 2 | 7
| CT Makeup Pump SIG JB #10 |  | 7 | 0 | 1 | 1 | 1 |  | 6 | 2 | 7
| Cooling Tower FAN SIG JB #10 |  | 4 | 0 | 1 | 0 |  |  | 5 | 2 | 6
| CT Plume Abatement System #10 |  | 5 |  | 16 | 6

## 5.2.1 PKG Inter. Cable (hidden)
[16 empty] | TOTAL IO | [8 empty] | TYPICAL IO
No. | Q'ty (A) | FROM |  |  |  |  | To |  |  |  |  | Communication |  |  |  | Total Field IO Q'ty |  |  |  | Total SWGR/MCC Interface IO |  |  |  | Total Typical Vibration / Gas detector | Typical Field IO Q'ty |  |  |  | Typical SWGR/MCC Interface IO |  |  |  | Typical Vibration / Gas detector
|  | Unit | Zone 1 EQ Description | Zone 1 SQ No. | Zone 1 Description | Zone 1 No. | Unit | Zone 2 EQ Description | Zone 2 SQ No. | Zone 2 Description | Zone 2 No. | Protocol | Cable Q'ty / Equipment | Cable Type | Remark | AI | AO | DI | DO | AI | AO | DI | DO | AI | AI | AO | DI | DO | AI | AO | DI | DO | AI

## 5.3.1 Comm. Cable (hidden)
Communication Cable Type
No. | EQ Q'ty (A) | FROM |  |  |  |  | TO |  |  |  |  | Protocol | Cable Q'ty (B) | Cable Type | Remark | Fiber Optic | Single Mode 6 core
|  | Unit | Zone 1 EQ Description | Zone 1 SQ No. | Zone 1 Description | Zone 1 No. | Unit | Zone 2 EQ Description | Zone 2 SQ No. | Zone 2 Description | Zone 2 No. |  |  |  |  | UTP
STP
RS485
Coaxial

## 5.4.2 Raceway (hidden)
Type | Description | Length | UNIT
Trench |  |  |  | Note
1. Refer to Main Cable Route issued by Elec. ENG
2. Refer to Length per raceway type informed by Elec. ENG
- Length shall be measured by I&C ENG if Elec. ENG not inform
Ductbaml
Tray

## 5.5 Cable Routing (hidden)
[7 empty] | 6 |  |  | 1
No. | From- | Zone 1 Description | Zone 1 No. | Zone 2 Description | Zone 2 No. | Total Cable Length (A=B+C+D+E) | Up & Down Cable (B) | Zone 1 side (C) | Zone 2 side (D) | Bending Length (E=F x L3) | ROUTE DISTANCE(m) (F) | ROUTE DISTANCE(m) (F) by N1 fx | ROUTE 1 | ROUTE 2 | ROUTE 3 | ROUTE 4 | ROUTE 5 | ROUTE 6 | ROUTE 7 | ROUTE 8 | ROUTE 9 | ROUTE 10 | ROUTE 11 | ROUTE 12 | ROUTE 13 | ROUTE 14 | ROUTE 15 | ROUTE 16 | ROUTE 17 | ROUTE 18 | ROUTE 19 | ROUTE 20
To