## 3.0_Valve List
VALVE LIST
Project : AL NOUF 1 PROJECT
RFQ NO. : D00P-00CZI00-J30-0001
DESCRIPTION : I&C Butterfly Valve
NO | P&ID NO. | VALVE TYPE | Q'ty | SYSTEM | UNIT NO. | SYSTEM CODE | SYSTEM SEQUENCE NO. | ITEM CODE | FIRST SEQUENCE NO. | TAG NUMBER | DESCRIPTION | SDT NO. (Design Table No.) | DESIGN CONDITION |  | FLUID | PIPE |  |  |  |  | BODY SIZE | VALVE RATING [#] | CONNECTION TYPE | TYPE |  |  |  |  | MATERIAL |  | FAIL POSITION | ACTUATOR TRAVEL TIME [SEC] | LEAKAGE CLASS | SET PRESSURE [barg] | MAKER | MODEL | EXPLOSION PROOF | REMARK | REMARK
[13 empty] | PRESSURE [barg] | TEMP [degC] |  | PMC CLASS | RATING | Material [ASTM] | NB [mm] | Sch. |  |  |  | ACTUATOR | OPERATION MODE | BODY | BONNET | TRIM | BODY | TRIM
1 | D00P-10PAC10-M05-0001 |  | 2 | P&ID FOR CIRCULATING WATER SYSTEM FOR GROUP 10 | [6 empty] | INLET WATERBOX 3 BUTTERFLY VALVE | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ① · 귀속 INLET WATERBOX 3
2 | D00P-10PAC10-M05-0001 |  | 2 | P&ID FOR CIRCULATING WATER SYSTEM FOR GROUP 10 | [6 empty] | BALL STRAINER WITH PDIT BUTTERFLY VALVE D | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ① · 귀속 BALL STRAINER WITH PDIT
3 | D00P-10PAC10-M05-0001 |  | 2 | P&ID FOR CIRCULATING WATER SYSTEM FOR GROUP 10 | [6 empty] | INLET WATERBOX 1 BUTTERFLY VALVE | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ① · 귀속 INLET WATERBOX 1
4 | D00P-10PAC10-M05-0001 |  | 2 | P&ID FOR CIRCULATING WATER SYSTEM FOR GROUP 10 | [6 empty] | BALL STRAINER WITH PDIT BUTTERFLY VALVE C | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ① · 귀속 BALL STRAINER WITH PDIT
5 | D00P-10PAC10-M05-0001 |  | 2 | P&ID FOR CIRCULATING WATER SYSTEM FOR GROUP 10 | [6 empty] | INLET WATERBOX 4 BUTTERFLY VALVE | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ① · 귀속 INLET WATERBOX 4
6 | D00P-10PAC10-M05-0001 |  | 2 | P&ID FOR CIRCULATING WATER SYSTEM FOR GROUP 10 | [6 empty] | BALL STRAINER WITH PDIT BUTTERFLY VALVE B | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ① · 귀속 BALL STRAINER WITH PDIT
7 | D00P-10PAC10-M05-0001 |  | 2 | P&ID FOR CIRCULATING WATER SYSTEM FOR GROUP 10 | [6 empty] | INLET WATERBOX 2 BUTTERFLY VALVE | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ① · 귀속 INLET WATERBOX 2
8 | D00P-10PAC10-M05-0001 |  | 2 | P&ID FOR CIRCULATING WATER SYSTEM FOR GROUP 10 | [6 empty] | BALL STRAINER WITH PDIT BUTTERFLY VALVE A | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ① · 귀속 BALL STRAINER WITH PDIT
9 | D00P-10LCA10-M05-0001 |  | 2 | P&ID FOR CONDENSATE SYSTEM GROUP 10 (1 OF 2) | [6 empty] | TO SAFE LOCATION BUTTERFLY VALVE | [12 empty] | PNEUMATIC |  | BUTTERFLY | [11 empty] | 판정축 ②b · 귀속 →SAFE LOCATION
10 | D00P-00PAB10-M05-0001 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (1 OF 3) | [6 empty] | TO GROUP #10 AUX. COOLING FROM AUXILIARY COOLING BUTTERFLY VALVE | [12 empty] | MOTOR |  | MOV(BUTTERFLY) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
11 | D00P-00PAB10-M05-0001 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (1 OF 3) | [6 empty] | TO TRAVELING BAND SCREEN D BUTTERFLY VALVE | [12 empty] | HYDRAULIC |  | HV(BUTTERFLY) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
12 | D00P-00PAB10-M05-0001 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (1 OF 3) | [19 empty] | HYDRAULIC |  | HV(BUTTERFLY) | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
13 | D00P-00PAB10-M05-0001 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (1 OF 3) | [6 empty] | TO EC & WT FEED WATER HEADER BUTTERFLY VALVE | [12 empty] | MOTOR |  | MOV(BUTTERFLY) | [11 empty] | 판정축 ②b · 귀속 →EC & WT FEED WATER HEADER
14 | D00P-00PAB10-M05-0002 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (2 OF 3) | [6 empty] | TO GROUP #20 AUX. COOLING FROM AUXILIARY COOLING BUTTERFLY VALVE | [12 empty] | MOTOR |  | MOV(BUTTERFLY) | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
15 | D00P-00PAB10-M05-0002 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (2 OF 3) | [19 empty] | MOTOR |  | MOV(BUTTERFLY) | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
16 | D00P-00PAB10-M05-0002 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (2 OF 3) | [19 empty] | HYDRAULIC |  | HV(BUTTERFLY) | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
17 | D00P-00PAB10-M05-0002 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (2 OF 3) | [6 empty] | SCREEM WASH PUMP DISCHARGE BUTTERFLY VALVE | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | 판정축 ③ · 귀속 SCREEM WASH PUMP→(다분기)
18 | D00P-00PAB10-M05-0002 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (2 OF 3) | [6 empty] | FROM SCREEM WASH PUMP BUTTERFLY VALVE A | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
19 | D00P-00PAB10-M05-0002 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (2 OF 3) | [6 empty] | FROM SCREEM WASH PUMP BUTTERFLY VALVE B | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
20 | D00P-00PAB10-M05-0002 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (2 OF 3) | [19 empty] | HYDRAULIC |  | HV(BUTTERFLY) | [11 empty] | [DESCRIPTION] 근거 없음 — 직접 입력 → 미처리
21 | D00P-00PAB10-M05-0003 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (3 OF 3) | [6 empty] | FROM SCREEN WASH PUMP BUTTERFLY VALVE | [12 empty] | MOTOR |  | BUTTERFLY | [11 empty] | [DESCRIPTION] 후보에서 골랐으나 근거가 약함 — 확인 필요 → 미처리
22 | D00P-00PAB10-M05-0003 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (3 OF 3) | [6 empty] | TO GROUP#20 AUXILIARY COOLING BUTTERFLY VALVE B | [12 empty] | MOTOR |  | MOV(BUTTERFLY) | [11 empty] | 판정축 ②b · 귀속 →GROUP#20 AUXILIARY COOLING
23 | D00P-00PAB10-M05-0003 |  | 1 | P&ID FOR SEAWATER INTAKE SYSTEM (3 OF 3) | [6 empty] | TO GROUP#20 AUXILIARY COOLING BUTTERFLY VALVE A | [12 empty] | MOTOR |  | MOV(BUTTERFLY) | [11 empty] | 판정축 ②b · 귀속 →GROUP#20 AUXILIARY COOLING
Note)
1. REFER TO ATTACHED REQUREMENT AND SPECIFICATION.
2. LEAKAGE CLASS: API 598
3. ENCLOSURE CLASS : IP67
4. ACTUATOR SHALL BE FITTED WITH A HANDWHEEL
5. ALL SIGNAL SHALL BE INTERFACED WITH DCS AS HARDWIRING
6. Refer to below specification for hydraulic unit.
1) HPU should be applied per each Hydraulic Valve.
2) Motor should be redundant. (2 x 100%)
3) Panel enclosure class : IP65.
4) Required hydraulic oil line should be included in bidder's scope of supply. (Each line could be considered as 20M)
5) Hydraulic oil should be included in bidder's scope of supply. (For flushing and initial operation)
7. Noise Level Limit : < 80 dB(A)
8. Actuator torque shall be calculated based on 125% of Design Pressure.
9. Cable gland, cable gland adaptor and plug shall be provided for Purchaser's cable connection.

## 5.2.0 PKG Inter. Typical (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | Field IO
|  |  | PKG Interface / Field - DCS IO |  |  |  | SWGR/MCC Interface IO |  |  |  | to VMS / Vibration(Triad) Gas Detector(Triad)
PKG Q'ty | PACKAGE | TYPE | AI | AO | DI | DO | AI | AO | DI | DO | AI
| GT TCS #10 | TCS
| ST TCS #10 | TCS
| CEMS #10 | PLC
| VMS (MEB) #10 | VMS
| VMS (CT LEB) #10 | VMS
| VMS (CCR) | VMS
| Intake System PLC | PLC
| Tube Cleaning System for Condenser | PLC
| Tube Cleaning System for CCW | PLC
| Air Compressor | PLC
| HRSG PLC | PLC
| WTP | PLC
| WWT | PLC
| Gas Chlorination System | PLC
| CPP | PLC
| DCS | DCS
| GIS | PLC
| CWMU Chlorination System | PLC
| CT Chlorination System | PLC
↑ Control System 적용 PKG
| GT TCS #10 |  | 11 | 5 | 19 | 19
| ST TCS #10 |  | 17 | 0 | 10 | 13
| CEMS #10 |  | 9 |  | 3
| SWAS for HRSG #10 |  | 62 |  | 5 | 9
| Condenser Tube Leak Detection#10 |  | 4 |  | 1
| SWAS for Condensate #10 |  | 28 |  | 5 | 4
| SWAS for CW #10 |  | 2 |  | 3
| SWAS for CW Return Line #10 |  | 2
| QMS for HRSG Blowdown #10 |  | 1 |  | 3
| QMS for Process Holding Pond #10 |  | 3 |  | 1
| QMS for Discharge water to Chao Phraya river #10 |  | 11 |  | 3
| VMS (MEB) #10 |  | 34 |  | 34
| VMS (CT LEB) #10 |  | 120 |  | 120
| Bypass Valve HPU for HP #10 |  | 1 |  | 3
| Bypass Valve HPU for IP/LP #10 |  | 1 |  | 3
| HRSG Transmitter #10 |  | 1
| HRSG Level Switch #10 |  |  | 1
| HRSG CV (AI&AO) #10 |  | 1 | 1
| HRSG CV (DI) #10 |  |  |  | 2
| HRSG XV #10 |  |  |  | 2 | 1
| HRSG MOV #10 |  |  |  | 6 | 2
| HRSG MOV Inching #10 |  |  |  | 6 | 2
| HRSG MOV Inching (AI) #10 |  | 1
| HRSG Analog JB #10 |  | 158 | 25
| HRSG Digital JB #10 |  |  |  | 238 | 73
| ESDV #10 |  | 1 | 0 | 6 | 3
| Fuel Gas Supply System #10 |  | 1
| FG Condensate Tank for GT Area #10 |  | 1
| Condenser Vacuum Pump #10 |  | 2 |  | 14 | 7
| CEP SIGNAL JB (Vibration/ Temp) #10 |  | 7 | 0 | 1 | 1 | 1 |  | 6 | 2 | 7
| BFP |  | 14 | 0 | 2 | 1 | 1 |  | 6 | 2 | 11
| CWP SIGNAL JB (Vib./Temp) #10 |  | 5 | 0 | 1 | 1 | 1 |  | 6 | 2 | 9
| CCWP SIG JB #10 |  | 7 | 0 | 1 | 1 |  |  | 5 | 2 | 7
| CT Makeup Pump SIG JB #10 |  | 7 | 0 | 1 | 1 | 1 |  | 6 | 2 | 7
| Cooling Tower FAN SIG JB #10 |  | 4 | 0 | 1 | 0 |  |  | 5 | 2 | 6
| CT Plume Abatement System #10 |  | 5 |  | 16 | 6

## 5.2.1 PKG Inter. Cable (hidden)
[16 empty] | TOTAL IO | [8 empty] | TYPICAL IO
No. | Q'ty (A) | FROM |  |  |  |  | To |  |  |  |  | Communication |  |  |  | Total Field IO Q'ty |  |  |  | Total SWGR/MCC Interface IO |  |  |  | Total Typical Vibration / Gas detector | Typical Field IO Q'ty |  |  |  | Typical SWGR/MCC Interface IO |  |  |  | Typical Vibration / Gas detector
|  | Unit | Zone 1 EQ Description | Zone 1 SQ No. | Zone 1 Description | Zone 1 No. | Unit | Zone 2 EQ Description | Zone 2 SQ No. | Zone 2 Description | Zone 2 No. | Protocol | Cable Q'ty / Equipment | Cable Type | Remark | AI | AO | DI | DO | AI | AO | DI | DO | AI | AI | AO | DI | DO | AI | AO | DI | DO | AI

## 5.3.1 Comm. Cable (hidden)
Communication Cable Type
No. | EQ Q'ty (A) | FROM |  |  |  |  | TO |  |  |  |  | Protocol | Cable Q'ty (B) | Cable Type | Remark | Fiber Optic | Single Mode 6 core
|  | Unit | Zone 1 EQ Description | Zone 1 SQ No. | Zone 1 Description | Zone 1 No. | Unit | Zone 2 EQ Description | Zone 2 SQ No. | Zone 2 Description | Zone 2 No. |  |  |  |  | UTP
STP
RS485
Coaxial

## 5.4.2 Raceway (hidden)
Type | Description | Length | UNIT
Trench |  |  |  | Note
1. Refer to Main Cable Route issued by Elec. ENG
2. Refer to Length per raceway type informed by Elec. ENG
- Length shall be measured by I&C ENG if Elec. ENG not inform
Ductbaml
Tray

## 5.5 Cable Routing (hidden)
[7 empty] | 6 |  |  | 1
No. | From- | Zone 1 Description | Zone 1 No. | Zone 2 Description | Zone 2 No. | Total Cable Length (A=B+C+D+E) | Up & Down Cable (B) | Zone 1 side (C) | Zone 2 side (D) | Bending Length (E=F x L3) | ROUTE DISTANCE(m) (F) | ROUTE DISTANCE(m) (F) by N1 fx | ROUTE 1 | ROUTE 2 | ROUTE 3 | ROUTE 4 | ROUTE 5 | ROUTE 6 | ROUTE 7 | ROUTE 8 | ROUTE 9 | ROUTE 10 | ROUTE 11 | ROUTE 12 | ROUTE 13 | ROUTE 14 | ROUTE 15 | ROUTE 16 | ROUTE 17 | ROUTE 18 | ROUTE 19 | ROUTE 20
To